## Sheet1
Max. flow through orifice plate (GPM) = | 250
Differential pressure at that flowrate (“WC) = | 100
(“k” factor) ---- Q = k * sqrt(P) = | 25
Differential pressure measurement error (“WC) = | -0.2
Yellow = values you enter into the spreadsheet
Blue = values calculated by the computer |  | Flow (GPM) | DP @ orifice (“WC”) | Displayed flow (GPM) | Flow error (GPM) | Flow error (% of actual GPM)
|  | 15 | 0.36 | 10 | -5 | -33.33%
|  | 25 | 1 | 22.3607 | -2.6393 | -10.56%
|  | 50 | 4 | 48.734 | -1.266 | -2.532%
|  | 75 | 9 | 74.162 | -0.83802 | -1.117%
|  | 100 | 16 | 99.373 | -0.62697 | -0.627%
|  | 125 | 25 | 124.499 | -0.501 | -0.4008%
|  | 150 | 36 | 149.5828 | -0.41725 | -0.2782%
|  | 175 | 49 | 174.6425 | -0.35751 | -0.2043%
|  | 200 | 64 | 199.6873 | -0.31274 | -0.1564%
|  | 225 | 81 | 224.7221 | -0.27795 | -0.1235%
|  | 250 | 100 | 249.7499 | -0.25013 | -0.1001%